Specification text for pressure media filter

Pos.	Quantity Description

1	0	Filter container

Closed filter containers as pressure media filter.

Filter container in cylindrical design

made of GRP fiberglass with dished top and dished bottom,

produced in the winding process, on a round GRP support

Inner fine layer made of chemical resistant special resin, vinyl ester.

Filter diameter inside approx. 1.300 mm

Media bed height 1.000 mm

Filter container height 1.800 mm

Height overall 1.950 mm

Operating pressure 2.5 bar

Water temperature up to 45 ° C

Equipment

1 revision on the top dome DN 400

1 manhole in the cylindrical part DN400

1 GRP flange for Ventilation DN 40

1 PVC flange for Raw water d140 with PVC funnel

Inner piping made of PVC d140

1 PVC outlet for pure water d140

1 GRP flange for purge air DN 40

All flanges drilled to PN 10, EN1092

1 nozzle plate made of GRP with support ring and supports made of GRP

with PP nozzles for water backwashing 103 pieces

Filter area 1.33 m2

Filter speed 30.0 m/h

Filter capacity 40 m3/h

MANUFACTURER Technol

MODEL Adriatic-N 130/c

Options against extra costs:

2 	0 	sight glass 4’’

3	0	Bigger inlet-outlet flanges

4 	0 	Filter container in split form delivered to the construction site

laminated together, reinforced and hardened.