Specification text for pressure media filter

Pos.	Quantity Description

1	0	Filter container

Closed filter containers as pressure media filter.

Filter container in cylindrical design

made of GRP fiberglass with dished top and dished bottom,

produced in the winding process, on a round GRP support

Inner fine layer made of chemical resistant special resin, vinyl ester.

Filter diameter inside approx. 1.800 mm

Media bed height 1.000 mm

Filter container height 1.850 mm

Height overall 2.050 mm

Operating pressure 2.5 bar

Water temperature up to 45 ° C

Equipment

1 revision on the top dome DN 400

1 manhole in the cylindrical part DN400

1 GRP flange for Ventilation DN 65

1 PVC flange for Raw water d160 with PVC funnel

1 PVC outlet for pure water DN 150

1 GRP flange for purge air DN 65

All flanges drilled to PN 10, EN1092

1 nozzle plate made of GRP with support ring and supports made of GRP

with PP nozzles for water backwashing ca. 204 pieces

Filter area 2.54 m2

Filter speed 30.0 m/h

Filter capacity 75 m3/h

MANUFACTURER Technol

MODEL Adriatic-N 180/c

Options against extra costs:

2 	0 	sight glass 4’’

3	0	Bigger inlet-outlet flanges

4 	0 	Filter container in split form delivered to the construction site

laminated together, reinforced and hardened.