Specification text for pressure media filter

Pos.	Quantity Description

1	0	Filter container

Closed filter containers as pressure media filter.

Filter container in cylindrical design

made of GRP fiberglass with dished top and dished bottom,

produced in the winding process, on a round GRP support.

Inner fine layer made of chemical resistant special resin, vinyl ester.

Filter diameter inside approx. 600 mm

Media bed height 1.000 mm

Filter container height 1.700 mm

Height overall 1.850mm

Operating pressure 2.5 bar

Water temperature up to 45 ° C

Equipment

1 revision on the top dome DN 200

1 manhole in the cylindrical part DN400

1 GRP flange for Ventilation DN 40

1 PVC flange for Raw water d63 with PVC funnel

Inner piping made of PVC d63

1 PVC outlet for pure water d63

1 GRP flange for purge air DN 40

All flanges drilled to PN 10, EN1092

1 nozzle plate made of GRP with support ring and supports made of GRP

with PP nozzles for water backwashing 21 pieces

Filter area 0.28 m2

Filter speed 30.0 m/h

Filter capacity 9 m3/h

MANUFACTURER Technol

MODEL Adriatic-N 60/c

Options against extra costs:

2 	0 	Sight glass 4’’

3	0 	Bigger Inlet-outlet flanges

3 	0 	Filter container in split form delivered to the construction site

laminated together, reinforced and hardened.