Specification text for pressure media filter

Pos.	Quantity Description

1	0	Filter container

Closed filter containers as pressure media

filter, design – according DIN 19 605 and DIN 19 643.

Filter container in cylindrical design

made of GRP fiberglass with dished top and dished bottom,

produced in the winding process, on a round GRP support

Inner fine layer made of chemical resistant special resin, vinyl ester.

Filter diameter inside approx. 1.400 mm

Cylindrical height 1.900 mm

Filter container height 2.600 mm

Height overall 2.750 mm

Operating pressure 2.5 bar

Water temperature up to 45 ° C

Equipment

1 revision on the top dome DN 400

1 manhole in the cylindrical part DN400

1 GRP flange for Ventilation DN 40

1 GRP flange for Raw water DN 125 with GRP funnel

Funnel diameter approx. 300 mm

Inner piping made of GRP DN 125

1 GRP outlet in the filter lower bottom with fixed flange for pure water DN 125

1 GRP flange for purge air DN 40

1 GRP flange with acrylic glass as sight glass DN 200

All flanges drilled to PN 10, EN1092

1 nozzle plate made of GRP with support ring and supports made of GRP

with PP nozzles for air & water backwashing 123 pieces

Filter area 1.54 m2

Filter speed 30.0 m/h

Filter capacity 46 m3/h

MANUFACTURER Technol

MODEL Mediterran 140/c

Options against extra costs:

2 	0 	sight glass consisting of:

1 GRP flange DN 200

1 acrylic glass cover DN 200

3	0	Sight glass suitable for the manhole

in the top dished end DN 400

1 acrylic glass cover DN 400

4 	0 	Filter container in split form delivered to the construction site

laminated together, reinforced and hardened.

5	 0 	PVC inner liner for protection against ozone